## HO Switch A
HO Switch A - Log entry | Description
973 34 2022-01-05 10:23:07 294d8h11m22s 192.0.11.100 admin Auth. ok | Log into switch to check the settings, Note down Switch port numbers
974 34 2022-01-05 14:01:13 294d11h49m27s 192.0.11.100 admin Auth. ok | As per change control login to switch
975 34 2022-01-05 14:01:28 294d11h49m42s Configuration change activated | Change 1- Switch A Port 1-7 and 1-8 is changed from Access port to Trunk port (VLAN 1 untagged and VLAN 40 Tagged)
976 34 2022-01-05 14:02:36 294d11h50m50s Configuration change activated | Change 2- Switch A Port 1-1 is changed from Access port to Trunk port (VLAN 1 untagged and VLAN 40 Tagged)
977 34 2022-01-05 14:04:50 294d11h53m4s Port 2-2 link off | As shown in Network built in diagram- Homesdale tunnel v.2.3, Port 2-2 is CPS office laptop. This needs to be confirmed by CPS whether this laptop is having any connectvity issues
978 34 2022-01-05 14:04:53 294d11h53m7s Port 2-2 link on
979 34 2022-01-05 14:46:26 294d12h34m40s Configuration change activated | Matthew Crooke mentioned SCADA client acnnot see the servers. Nodes in Tunnel VLAN are not abel to see each other. Change 3- During the dsciussion with Matthew Crooke - PDS, I explained all the changes required for optasense VLAN and this changes should not have any impact for PDS Tunnel VLAN (VLAN 10). Matthew said PDS VLAN 10 is tagged in Bellcommon between the swithes. He mentioned HO SCADA clients are not able to see servers in tunnel VLAN (VLAN 10). To fix this issue, we agreed to add VLAN 10 in trunk ports. This caused a broadcast storm causing the PLC's to not responding.
980 34 2022-01-05 14:53:42 294d12h41m56s Configuration change activated | Matt mentioned we cannot conitnue any works and it shoudl be stopped. Change 4- Restore to old configuration Switch A Port 1-7 and 1-8 is changed from Trunk port to Access port (VLAN 1 untagged ) Switch A Port 1-1 is changed from Trunk port to Access port (VLAN 1 untagged )
981 34 2022-01-05 15:08:39 294d12h56m53s Port 2-2 link off | As shown in Network built in diagram- Homesdale tunnel v.2.3, Port 2-2 is CPS office laptop. This needs to be confirmed by CPS whether this laptop is having any connectvity issues
982 34 2022-01-05 15:08:41 294d12h56m55s Port 2-2 link on
983 34 2022-01-05 15:09:06 294d12h57m20s Port 2-2 link off
984 34 2022-01-05 15:09:08 294d12h57m22s Port 2-2 link on
985 34 2022-01-05 16:03:48 294d13h52m1s 192.0.11.100 admin Auth. ok | Login to switch to check the event logs
986 34 2022-01-05 16:39:24 294d14h27m38s Port 1-3 link off | Mac address of this device suggets it’s a node form manufacturer- Vmware Inc, PDS needs to confirm what is this?
987 34 2022-01-05 16:39:26 294d14h27m40s Port 1-3 link on
988 34 2022-01-05 16:39:31 294d14h27m45s Port 1-3 link off
989 34 2022-01-05 16:39:33 294d14h27m47s Port 1-3 link on
990 34 2022-01-05 16:40:07 294d14h28m21s Port 1-3 link off
991 34 2022-01-05 16:40:09 294d14h28m23s Port 1-3 link on
992 34 2022-01-05 16:40:10 294d14h28m24s Port 1-3 link off
993 34 2022-01-05 16:40:12 294d14h28m26s Port 1-3 link on
994 34 2022-01-05 16:40:15 294d14h28m29s Port 1-3 link off
995 34 2022-01-05 16:40:17 294d14h28m31s Port 1-3 link on
996 34 2022-01-05 16:40:29 294d14h28m43s Port 1-3 link off
997 34 2022-01-05 16:40:30 294d14h28m44s Port 1-3 link on
998 34 2022-01-05 16:40:53 294d14h29m6s Port 1-3 link off
999 34 2022-01-05 16:40:54 294d14h29m7s Port 1-3 link on
1000 34 2022-01-05 17:33:33 294d15h21m46s 192.0.11.100 admin Auth. ok | Login into switch to check event logs

## HO Switch B
HO Switch B - Log entry | Description
687 26 2022-01-05 10:20:09 2847d14h18m18s 192.0.11.100 admin Auth. ok | Log into switch to check the settings, Note down Switch port numbers
688 26 2022-01-05 13:59:54 2847d17h58m2s 192.0.11.100 admin Auth. ok | As per change control login to switch
689 26 2022-01-05 14:00:52 2847d17h59m1s Configuration change activated | Change 1- Switch A Port 1-7 and 1-8 is changed from Access port to Trunk port (VLAN 1 untagged and VLAN 40 Tagged)
690 26 2022-01-05 14:02:01 2847d18h0m10s Configuration change activated | Change 2- Switch A Port 1-1 is changed from Access port to Trunk port (VLAN 1 untagged and VLAN 40 Tagged)
691 26 2022-01-05 14:46:01 2847d18h44m9s Configuration change activated | Matthew Crooke mentioned SCADA client acnnot see the servers. Nodes in Tunnel VLAN are not abel to see each other. Change 3- During the dsciussion with Matthew Crooke - PDS, I explained all the changes required for optasense VLAN and this changes should not have any impact for PDS Tunnel VLAN (VLAN 10). Matthew said PDS VLAN 10 is tagged in Bellcommon between the swithes. He mentioned HO SCADA clients are not able to see servers in tunnel VLAN (VLAN 10). To fix this issue, we agreed to add VLAN 10 in trunk ports. This caused a broadcast storm causing the PLC's to not responding.
692 26 2022-01-05 14:53:33 2847d18h51m41s Configuration change activated | Matt mentioned we cannot conitnue any works and it shoudl be stopped. Change 4- Restore to old configuration Switch A Port 1-7 and 1-8 is changed from Trunk port to Access port (VLAN 1 untagged ) Switch A Port 1-1 is changed from Trunk port to Access port (VLAN 1 untagged )
693 26 2022-01-05 16:22:21 2847d20h20m29s Configuration change activated | Change 5- IT4A disbaled the ports 1-2 as troubleshooting procedure to check what is connected on this port
694 26 2022-01-05 16:22:28 2847d20h20m36s Configuration change activated | Change 6- IT4A enabled the ports 1-2 as troubleshooting procedure to check what is connected on this port
695 26 2022-01-05 16:38:55 2847d20h37m3s 192.0.11.100 admin Auth. ok | Login to switch to check the event logs
696 26 2022-01-05 16:39:26 2847d20h37m33s Port 2-2 link off | Mac address of this device suggets it’s a node form manufacturer- Dell & Vmware Inc, PDS needs to confirm what is this?
697 26 2022-01-05 16:39:27 2847d20h37m34s Port 2-2 link on
698 26 2022-01-05 16:39:33 2847d20h37m40s Port 2-2 link off
699 26 2022-01-05 16:39:35 2847d20h37m42s Port 2-2 link on
700 26 2022-01-05 16:40:08 2847d20h38m16s Port 2-2 link off
701 26 2022-01-05 16:40:09 2847d20h38m17s Port 2-2 link on
702 26 2022-01-05 16:40:11 2847d20h38m19s Port 2-2 link off
703 26 2022-01-05 16:40:12 2847d20h38m20s Port 2-2 link on
704 26 2022-01-05 16:40:15 2847d20h38m23s Port 2-2 link off
705 26 2022-01-05 16:40:16 2847d20h38m24s Port 2-2 link on
706 26 2022-01-05 16:40:30 2847d20h38m38s Port 2-2 link off
707 26 2022-01-05 16:40:31 2847d20h38m39s Port 2-2 link on
708 26 2022-01-05 16:40:52 2847d20h39m0s Port 2-2 link off
709 26 2022-01-05 16:40:54 2847d20h39m2s Port 2-2 link on